## Summary sheet
Sr. No. | Description of Works | Total Amt rs.
1
i | VRF HIGH SIDE (IMPORTED ITEMS) | 0
ii | VRF LOW SIDE | 0
| GRAND TOTAL OF HVAC Works | 0
| GST @ 18% | 0 | s
| GRAND TOTAL OF HVAC Works with Taxes | 0

## High SIde
Sr. No. | Description of Works | Total Qty | Unit | Rate | Amount
1 | SECTION - I ' VRF HIGH SIDE"
1
Supply of VRF Condensing Units of following actual capacities with inverter scroll compressor , necessary interlocks & R 410 A Refrigerant
i | 44HP 22 X 2 | 1 | Nos.
ii | 10 HP | 1 | Nos.
2 | Supply of Indoor Cassette Units with necessary 1 way & 4 way grill /micro-controller, drain pump , provision for fresh air Connection etc. of following configuration
i | 0.8 TR capacity (Four Way Compact Cassette Unit) | 3 | Nos.
ii | 1.0 TR capacity (One Way Compact Cassette Unit) | 3 | Nos.
iii | 1.5 TR capacity (One Way Compact Cassette Unit) | 5 | Nos.
iv | 2.0 TR capacity (Four Way Normal Cassette Unit) | 8 | Nos.
v | 2.5 TR capacity (Four Way Normal Cassette Unit) | 0 | Nos.
vi | 3.0 TR capacity (Four Way Normal Cassette Unit) | 2 | Nos.
vii | 4.0 TR capacity (Four Way Normal Cassette Unit) | 0 | Nos.
2a | Supply of VRF Indoor Highwall Units with necessary grill /micro-controller, corded remote etc. Supply of Indoor Units of following configuration
i | 2.0 TR capacity | - | Nos.
ii | 1.5TR capacity | - | Nos.
iii | 1.0 TR capacity | - | Nos.
3 | Supply of Treated Fresh Air Unit Supply of Indoor Units of following configuration
i | 8TR Ductable | 1 | Nos.
4 | Supply of Wired Remote Controller for all indoor & TFA Units | 23 | Nos.
5 | Supply of extra cable for Wired Remote Controller for all units. | 100 | Mtr
6 | Supply of centralised remote controller for all indoor units on the floor and should be installed in a Control Room. With On /OFF, reading and monitoring provision. It shall have display for displaying all the relevant data. | 1 | Nos.
7 | Supply of Centralized Monitoring Hardware with L.C.D display for Operator interface to Manage Entire VRV System from Single point for Whole Building & to be installed in BMS / Server Room. The following controls should be possible through this system:- 1) Temperature Controls, 2) Swing Control, 3) ON/OFF Control, 4) Scheduling, 5) Monitoring & Control from a remote site by Web Browser. 6) Sends Malfunction report through Internet by E-Mail. 7) Complaint with RoHS Directive. 8) Energy Saving Function. | - | Set
8 | Supply of Hi Wall type of DX unit with following capacities, with air-cooled condensing units & inverter compressor with green gas & necessary micro controller, drain pump and remote control for individual units with all standard accessories .(5 Star BEE Rating)
i | 2.0TR capacity (Hiwall unit ) | - | Nos.
ii | 1.5TR capacity (Hiwall unit) | - | nos.
iii | 1.0 TR capacity (Hiwall Unit) | - | Nos.
1 | SECTION - I TOTAL CARRIED OVER TO SUMMARY SHEET |  |  |  | 0

## Low Side
No. |  | Qty |  | Rate | Amount
2 | SECTION - II ' VRF LOW SIDE"
1 | Installation of Outdoor Units with additional refrigerant charge as per installed piping length & unit capacities, duly painted MS Stand with 1 coat of anti-corrosive paint and 2 coats of colour paint with same colour & shade of ODU, of following Configuration & it's Pressure Testing, Nitrogen flushing, Gas charging & Commissioning testing in all respect.
i | 44 HP (18X3) | 1 | Nos.
ii | 10 HP | 1 | Nos.
iii | Stand for ODU | 3 | Nos.
2 | Installation & Commissioning of Indoor Unit VRF's / Inverter type of Following types. The scope includes the GI threaded rod of required dia to hang the Ducted / FCU / cassette units and required fabrication with MS Channel duly painted with anti corrosive primer and 2 coats of paint. The FCU should include the Double Canvass Connection with necessary flanges and zip for inspection..
i | High Wall Units / Cassette Units /HRU Unit | 23 | Nos.
3 | Installation, Testing & Commissioning of centralised remote controller for all indoor unit and should be installed in a Control Room, with On /OFF provision, Temp setting with its necessary connecting and control cable, all necessary hard ware & software. | 1 | Nos.
4 | Supply, Installation, Testing & Commissioning of HiWall / Cassette Type Split AC Units with Ribbed Rubber Pads, Flexible connection for Drain, Green Gas and mild steel condenser stand for Air cooled Hi Wall Split unit. The charges should also include Nitrogen Flushing, Pressure Testing, Vacuum etc.(Condenser Stand Wall mount) | - | Nos.
5 | Supply, Installation, Testing & Commissioning of 19 G Copper Refrigerant Piping with 19 mm thick Closed Cell rubber nitrile, Class "O"- armaflex insulation of following sizes- Inclusive of necessary Supports with Ladder type cable tray as per standard practices. For Pipes Exposed to Atmosphere - Treatment of Piping with Woven Glass Cloth , ~ 100 gsm, finished in U/V Treated, pigmented Epoxy for Outdoor Piping, as per code. necessary pipe sizing to be done by successful bidder. Cable tray Cover required over ladder type cable tray in shafts and wherever copper piping is exposed to atmosphere. Nitrogen bleeding to be carried while brazing of refnut and piping joints as per OEM's standard procedure.
Gas Line (in mm.) Liquid Line (in mm.)
i | 41.3 19.1 | 30 | Rmt.
ii | 34.9 19.1 | 25 | Rmt.
iii | 28.6 15.9 | 25 | Rmt.
iv | 28.6 12.7 | 20 | Rmt.
v | 22.2 12.7 | 95 | Rmt.
vi | 19.1 9.5 | 20 | Rmt.
vii | 15.9 9.5 | 50 | Rmt.
viii | 12.7 6.4 | 60 | Rmt.
No. |  | Qty |  | Rate | Amount
6 | Supply, Installation, Testing & Commissioning of Interconnecting copper shielded control cabling between IDU's & ODU's. The cabling shall be well supported / tied up with the ref line. In PVC conduits of Black colour with Junction boxes required as per the indoor unit locations. | 370 | Rmt.
6.1 | supply cable for ODU 16sqmmx 5C | 19 | Rmt.
7 | Supply, Installation, Testing & Commissioning of Refrigerant Piping For the Following machines using 16 Gauge Hard Drawn Copper pipes as under. The distances between the indoor & outdoor units would be mentioned. The contractor would be paid on the basis of the distance between indoor & outdoor unit. The contractor should quote the rate including all the circuits, proper saddling of the piping should be carried out as per the spec. The contractor should use appropriate size pipes for each circuit with appropriate thickness nitrile rubber insulation. Maximum allowable supporting distance of copper pipes shall be 1000 mm.
i | 2.0 TR capacity (Hiwall Unit) | - | Rmt.
ii | 1.5 TR capacity (Hiwall Unit) | - | Rmt.
iii | 1.0 TR capacity (Hiwall Unit) | - | Rmt.
8 | Supply, Installation, Testing & Commissioning of Refrigerant piping joints for VRV / VRF system as per the manufacturers std. & has to be supplied with system and insulation of ref-nut profile only. As required for Gas & Liquid line. | 25 | Nos
9 | Supply, Installation, Testing & Commissioning of Drain Piping shall be HARD PVC . 25mm dia for single unit, 40mm dia for two units and 50mm dia for 3 units. Drain Piping shall be insulated 13mm Armaflex rubber nitrile closed cell insulation. The drain shall be released as per tender layout. 'U'-Traps to be provided at each individual units. G.I Threaded rod supports with Clevis clamps at a distance of maximum 1000mm.
i | 50 mm dia. | 60 | Rmt.
ii | 32 mm dia. | 60 | Rmt.
iii | 25 mm dia. | 80 | Rmt.
10 | Supply, Installation, Testing & Commissioning of hi capacity drain pumps for Hiwall units. | - | Nos.
11 | Supply, Installation, Testing & Commissioning of Preinsulated flexible duct with end clamps and Aluminium foil on both side as required in various sizes as below. The duct shall fire retardant UL standard approved.
i | 100 - mm Dia | 30 | Rmt.
ii | 150 - mm Dia | - | Rmt.
iii | 200- mm Dia | 14 | Rmt.
12 | Supply, Installation, Testing & Commissioning of Automatic Duct flow controllers, for fresh air control at cassettes ; ductables & specific location marked on the drawing. | - | Nos.
13 | Supply, Fabrication, Installation & testing of GI Spiral Ducting (Factory Fabricated) with T.D.Flange as per SMACNA Class-2. including Gripple supports as per SMACNA standards and ducts to be properly sealed along the Joints & Flanges with approved sealants including smoke leakage test etc. complete. Note : No slip joints allowed.
i | 18 Gauge | - | Sq.M.
ii | 20 Gauge | - | Sq.M.
iii | 22 Gauge | - | Sq.M.
iv | 24 Gauge | 220 | Sq.M.
No. |  | Qty |  | Rate | Amount
14 | Supply, Installation, Testing & Commissioning of Thermal Insulation of duct with 19 mm thick Nitrile Rubber with Anti Microbial Treatment & Better Thermal Conductivity & Moisture Diffusion Resistance & of Class 'O' stuck to the duct using rubber adhesives.(F.M. Approved). Density 45 - 55 kg/m3. | 220 | Sq.M.
15 | Supply, Installation, Testing & Commissioning of Acoustic Insulation of duct with 15 mm thick Open Cell Nitrile Rubber with Anti Microbial Treatment & of Class '1' stuck inside the duct using rubber adhesives.(F.M. Approved). Density of 140 - 180 Kg/m3. | 10 | Sq.M.
16 | Supply, Installation, Testing & Commissioning of Factory fabricated Aero foil type Volume Control Damper made out of GI material (1.5 mm thick) 18 Gauge GI Frame, 18 Gauge Al aerofoil blades with compressible jamb seals and in opposed-blade arrangement with steel operating rods rotating in nylon bearings mounted in a single frame, Leakage rate shall not exceed 2 percent of air quantity at 10 m/s face velocity through damper and 100 mm W.C. pressure differential. Provide engraved type “OPEN & CLOSE” indication. Refer to the drawings for various sizes required. The VCD shall have TDF flanges which suitable to connect with duct. | 2 | Sq.M.
No. |  | Qty |  | Rate | Amount
17 | Supply, Installation, Testing and Commissioning of Motorised Class II Fire Damper as per UL555s (Sealed & Stamped) with outer shell of 1.6 mm thick galvanised steel frame and the blade/leaf of 1.6 mm thick GSS. And the necessary flanges for connection as per specification. The damper shall be 120 min fire raring. With spring return actuator working on 220 V AC and each fire damper should be supplied with necessary High torque spring return actuator & control panel. The control panel, indicator, auxiliary contacts, necessary power and control cabling, position feedback, relay position for remote control operation etc. as per drawing & specifications. The control panel should be capable to operate the damper through BMS for remote control operation & monitoring. The number of Actuators per damper shall be selected based on the area & dimensions of the damper. For larger dampers, the number of actuators per damper can be selected 2 or more based on manufacturer selection to ensure smooth & reliable operation. Necessary power & control contactors with power & control cabling shall be considered. | - | Sq.M.
18 | Supply, Installation, Testing & Commissioning of Fire dampers min 120 min rating,with fusible link & of GI Construction, as per the attached technical specifications. | 0 | Sq.M.
19 | Supply, Installation, Testing & Commissioning of Timer Scheduler for Hiwall Units. | - | Nos.
20 | Supply, Installation, Testing & Commissioning of Aluminium Powder coated louvers with Al mesh inside the louver | - | Sq.M.
21 | Supply, Installation, Testing & Commissioning of Underdeck Roof insulation with 19 mm thick Nitrile rubber insulation with Aluminium foil on one side. | - | Sq.M.
22 | Supply, Installation, Testing & Commissioning of All side Flanged Grille with peanum box& Al. damper made out Extruded Aluminium duly powder coated of following size:
i | Grille: 300 x300 | 7 | Sq.M.
ii | Grille: 200 x 200 | - | Sq.M.
23 | Supply and installation of readymade 16SWG, GI Ladder/ Perforated trays of following size of 75mm / 50 mm depth unless otherwise specified including readymade accessories e.g. Vertical, horizontal bends, tee's, right-angle etc readymade GI clamps / supports for fixing the cable trays. Along with Supply and installation of readymade GI tray covers 16/18 SWG including readymade shape of Vertical & Horizontal Bend, Tee's, Right angles etc. to suit tray for all vertical & Horizontal runs.
i | 600mm Width | 120 | Rmt.
ii | 450mm Width | 30 | Rmt.
iii | 300mm Width | 30 | Rmt.
iv | 150mm Width | 15 | Rmt.
24 | Supply, Fabrication and Installation of M.S. angle / channel supports for trays & copper piping and drain pipes, wall mounting of panels or indoor units, frames, steel support over trench etc. including necessary painting with 2 coats of primer & 2 coats of enamel paint, & required hardware for fixing of supports etc. complete. | 400 | Kg.
25 | Lifting shifting Crane charges of ODUs IDUs ground to first floor / ground to third floor | 1 | lot
2 | SECTION - II TOTAL CARRIED OVER TO SUMMARY SHEET |  |  |  | 0